## Slide 1: ECE 476 Power System Analysis
Lecture 10: Per Unit, Three-Phase Transformers, Load and Generators
Prof. Tom Overbye
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
overbye@illinois.edu

## Slide 2: Announcements
Please read Chapter 2.4, Chapter 6 up to 6.6
HW 4 is due now; HW 5 is 5.31, 5.43, 3.4, 3.10, 3.14, 3.19, 3.23, 3.60, 6.30 should be done before exam 1
Exam 1 is Thursday Oct 6 in class
  Closed book, closed notes, but you may bring one 8.5 by 11 inch note sheet and standard calculators
  Last name A-M here, N to Z in ECEB 1013
Power Area Scholarships, Awards (Oct 1 deadlines, except Nov 1 for Grainger)
  http://energy.ece.illinois.edu/
  Turn both into Prof Sauer (4046 or 4060)

## Slide 3: Service Entrance Grounding
Image: www.osha.gov/dte/library/electrical/electrical_10.gif
We’ll talk more about grounding later in the semester when we cover faults

## Slide 4: Per Unit Calculations
A key problem in analyzing power systems is the large number of transformers.
  It would be very difficult to continually have to refer impedances to the different sides of the transformers
This problem is avoided by a normalization of all variables.
This normalization is known as per unit analysis.

## Slide 5: Per Unit Conversion Procedure, 1f
Pick a 1f VA base for the entire system, SB
Pick a voltage base for each different voltage level, VB. Voltage bases are related by transformer turns ratios. Voltages are line to neutral.
Calculate the impedance base, ZB= (VB)2/SB
Calculate the current base, IB = VB/ZB
Convert actual values to per unit
Note, per unit conversion on affects magnitudes, not
the angles. Also, per unit quantities no longer have
units (i.e., a voltage is 1.0 p.u., not 1 p.u. volts)

## Slide 6: Per Unit Solution Procedure
Convert to per unit (p.u.) (many problems are already in per unit)
Solve
Convert back to actual as necessary

## Slide 7: Per Unit Example
Solve for the current, load voltage and load power
in the circuit shown below using per unit analysis
with an SB of 100 MVA, and voltage bases of
8 kV, 80 kV and 16 kV.
Original Circuit

## Slide 8: Per Unit Example, cont’d
Same circuit, with
values expressed
in per unit.

## Slide 9: Per Unit Example, cont’d

## Slide 10: Per Unit Example, cont’d
To convert back to actual values just multiply the
per unit values by their per unit base

## Slide 11: Three Phase Per Unit
Pick a 3f VA base for the entire system,
Pick a voltage base for each different voltage level, VB. Voltages are line to line.
Calculate the impedance base
Procedure is very similar to 1f except we use a 3f
VA base, and use line to line voltage bases
Exactly the same impedance bases as with single phase!

## Slide 12: Three Phase Per Unit, cont'd
Calculate the current base, IB
Convert actual values to per unit
Exactly the same current bases as with single phase!

## Slide 13: Three Phase Per Unit Example
Solve for the current, load voltage and load power
in the previous circuit, assuming a 3f power base of
300 MVA, and line to line voltage bases of 13.8 kV,
138 kV and 27.6 kV (square root of 3 larger than the 1f example voltages). Also assume the generator is Y-connected so its line to line voltage is 13.8 kV.
Convert to per unit
as before. Note the
system is exactly the
same!

## Slide 14: 3f Per Unit Example, cont'd
Again, analysis is exactly the same!

## Slide 15: 3f Per Unit Example, cont'd
Differences appear when we convert back to actual values

## Slide 16: 3f Per Unit Example 2
Assume a 3f load of 100+j50 MVA with VLL of 69 kV is connected to a source through the below network:
What is the supply current and complex power?
Answer: I=467 amps, S = 103.3 + j76.0 MVA

## Slide 17: Per Unit Change of MVA Base
Parameters for equipment are often given using power rating of equipment as the MVA base
To analyze a system all per unit data must be on a common power base

## Slide 18: Per Unit Change of Base Example
A 54 MVA transformer has a leakage reactance of 3.69%. What is the reactance on a 100 MVA base?

## Slide 19: Transformer Reactance
Transformer reactance is often specified as a percentage, say 10%. This is a per unit value (divide by 100) on the power base of the transformer.
Example: A 350 MVA, 230/20 kV transformer has leakage reactance of 10%. What is p.u. value on 100 MVA base? What is value in ohms (230 kV)?

## Slide 20: Three Phase Transformers
There are 4 different ways to connect 3f transformers
Y-Y
D-D
Usually 3f transformers are constructed so all windings
share a common core

## Slide 21: 3f Transformer Interconnections
D-Y
Y-D

## Slide 22: Y-Y Connection

## Slide 23: Y-Y Connection: 3f Detailed Model

## Slide 24: Y-Y Connection: Per Phase Model
Per phase analysis of Y-Y connections is exactly the same as analysis of a single phase transformer.
Y-Y connections are common in transmission systems.
Key advantages are the ability to ground each side
and there is no phase shift is introduced.

## Slide 25: D-D Connection

## Slide 26: D-D Connection: 3f Detailed Model
To use the per phase equivalent we need to use
the delta-wye load transformation

## Slide 27: D-D Connection: Per Phase Model
Per phase analysis similar to Y-Y except impedances are decreased by a factor of 3.
Key disadvantage is D-D connections can not be grounded; not commonly used.

## Slide 28: D-Y Connection

## Slide 29: D-Y Connection V/I Relationships

## Slide 30: D-Y Connection: Per Phase Model
Note: Connection introduces a 30 degree phase shift!
Common for transmission/distribution step-down since
there is a neutral on the low voltage side.
Even if a = 1 there is a sqrt(3) step-up ratio

## Slide 31: Y-D Connection: Per Phase Model
Exact opposite of the D-Y connection, now with a
phase shift of -30 degrees.

## Slide 32: Load Tap Changing Transformers
LTC transformers have tap ratios that can be varied to regulate bus voltages
The typical range of variation is 10% from the nominal values, usually in 33 discrete steps (0.0625% per step).
Because tap changing is a mechanical process, LTC transformers usually have a 30 second deadband to avoid repeated changes.
Unbalanced tap positions can cause "circulating vars"

## Slide 33: LTCs and Circulating Vars

## Slide 34: Phase Shifting Transformers
Phase shifting transformers are used to control the phase angle across the transformer
  Also called phase angle regulators (PARs) or quadrature booster transformers
Since power flow through the transformer depends upon phase angle, this allows the transformer to regulate the power flow through the transformer
Phase shifters can be used to prevent inadvertent "loop flow" and to prevent line overloads.
Image Source: en.wikipedia.org/wiki/Quadrature_booster#/media/File:Qb-3ph.svg

## Slide 35: Phase Shifter Example 3.13

## Slide 36: Autotransformers
Autotransformers are transformers in which the primary and secondary windings are coupled magnetically and electrically.
This results in lower cost, and smaller size and weight.
The key disadvantage is loss of electrical isolation between the voltage levels. Hence auto-transformers are not used when a is large. For example in stepping down 7160/240 V we do not ever want 7160 on the low side!