## Slide 1: ECE 530 – Analysis Techniques for Large-Scale Electrical Systems
Prof. Hao Zhu
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
haozhu@illinois.edu
10/19/2015
Lecture 14: Sensitivity Analysis

## Slide 2: Announcements
Midterm exam is October 21 in class; closed book and notes, but one letter-sized note sheet and simple calculators allowed
  Test covers up to dc power flow (everything before today’s lecture)

## Slide 3: Sensitivity Analysis
System description and notation
Motivation for the sensitivity analysis
From sensitivity to distribution factors
Definitions of the various distribution factors
Analysis of the distribution factors
Distribution factor applications

## Slide 4: Notation
We consider a system with N buses and L lines given by the set given by the set
  Some authors designate the slack as bus zero; an alternative approach, that is easier to implement in cases with multiple islands and hence slacks, is to allow any bus to be the slack, and just set its associated equations to trivial equations just stating that the slack bus voltage is constant
We may denote the kth transmission line or transformer in the system, , as , ),
from node
to node

## Slide 5: Notation, cont.
We’ll denote the real power flowing on line from bus to bus as
The vector of active power flows on the L lines is:
The bus real and reactive power injection vectors are (note we use lower-case p/q injection in later analysis)
p

## Slide 6: Notation, cont.
The series admittance of line is , and we define the matrix
We define the LN incidence matrix:
where all elements of vector ak are zero, except for that and , as line is coincident with these buses. Hence matrix A is quite sparse, with two nonzeros per row

## Slide 7: Analysis Example: Available Transfer Capability
The power system available transfer capability (ATC) is defined as the maximum additional MW that can be transferred between two specific areas, while meeting all the specified pre- and post-contingency system conditions
ATC impacts measurably the market outcomes and system reliability and, therefore, the ATC values impact the system and market behavior
A useful reference on ATC is Available Transfer Capability Definitions and Determination from NERC, June 1996 (available freely online)

## Slide 8: ATC and Its Key Components
Total transfer capability (TTC )
  Amount of real power that can be transmitted across an interconnected transmission network in a reliable manner, including considering contingencies
Transmission reliability margin (TRM)
  Amount of TTC needed to deal with uncertainties in system conditions; typically expressed as a percent of TTC
Capacity benefit margin (CBM)
  Amount of TTC needed by load serving entities to ensure access to generation; typically expressed as a percent of TTC

## Slide 9: ATC and Its Key Components
Uncommitted transfer capability (UTC)
UTC = TTC – existing transmission commitments
Formal definition of ATC is
ATC = UTC – CBM – TRM
We focus on determining Um,n, the UTC from node m to node n, defined as the maximum additional MW that can be transferred from node m to node n without violating any limit in either the base case or in any post-contingency conditions

## Slide 10: UTC Evaluation
no
limit violation
for the base case j = 0 and each contingency case
j = 1,2 … , J

## Slide 11: Conceptual Solution Algorithm
Solve the initial power flow, corresponding to the initial system dispatch (i.e., existing commitments); Initialize the change in transfer  t(0) = 0, k =0; set step size d ; j is used to indicate either the base case (j=0) or a contingency, j = 1,2,3…J
Compute  t(k+1) =  t(k) + d
Solve the power flow for the new  t(k+1)
Check for limit violations:
if violation is found set U(j)m,n =  t(k) and stop;
else set k = k+1, and goto 2

## Slide 12: Conceptual Solution Algorithm, cont.
This algorithm is applied for the base case (j=0) and each specified contingency case, j=1,2,..J
The final UTC, Um,n is then determined by
This algorithm can be easily performed on parallel processors since each contingency evaluation is independent of the other

## Slide 13: Five Bus Example: Base Case
PowerWorld Case: B5_DistFact

## Slide 14: Five Bus Network Data
 |  |  |  |  | ( MW )
 | 1 | 2 | 0 | -6.25 | 150
 | 1 | 3 | 0 | -12.5 | 400
 | 1 | 4 | 0 | -12.5 | 150
 | 2 | 3 | 0 | -12.5 | 150
 | 3 | 4 | 0 | -12.5 | 150
 | 4 | 5 | 0 | -10 | 1,000

## Slide 15: Five Bus UTC
We evaluate U2,3 using the previous procedure
  Gradually increase generation at Bus 2 and load at Bus 3
We consider the base case and a single contingency with line 2 outaged (between 1 and 3): J = 1
Simulation results show for the base case that
And for the contingency that
Hence

## Slide 16: UTC: Base Case

## Slide 17: UTC: Contingency Case

## Slide 18: Computational Considerations
Obviously such a brute force approach can run into computational issues with large systems
Consider the following situation:
  10 iterations for each case
  6,000 contingencies
  2 seconds to solve each power flow
It will take over 33 hours to compute a single UTC for the specified transfer direction from m to n.
Consequently, there is an urgent need to develop fast tools that can provide satisfactory approximations

## Slide 19: Problem Formulation
Denote the system state by
Denote the conditions corresponding to the existing commitment/dispatch by x(0), p(0) and f(0) so that
the power flow equations
line active power flow vector
with

## Slide 20: Problem Formulation
where
constant

## Slide 21: First-order Approximation
For a small change, p, that moves the injection from p(0) to p(0) + p , we have a corresponding change in the state x satisfying
We apply a first-order Taylor’s series expansion as

## Slide 22: First-order Approximation
We consider this to be a “small signal” change, so we can neglect the h.o.t. in the expansion
Hence, in order to satisfy the power balance equations with this perturbation, it follows that

## Slide 23: Jacobian Matrix
Also, using the nonlinear power flow equations, we obtain
and then the power flow Jacobian

## Slide 24: Flow Sensitivity Matrix
With the standard assumption that the power flow Jacobian is nonsingular, then
We can then compute the change in the line real power flow vector
the flow sensitivity matrix

## Slide 25: Sensitivity Comments
Sensitivities can easily be calculated even for large systems
  If p is sparse (just a few injections) then we can use a fast forward; if sensitivities on a subset of lines are desired we could use a fast backward
Sensitivities are dependent upon the operating point
  Also they include the impact of marginal losses
Sensitivities could easily be expanded to include additional variables in x (such as phase shifter angle), or additional equations, such as reactive power flow

## Slide 26: Sensitivity Comments, cont.
Sensitivities are used in the optimal power flow; in that context a common application is to determine the sensitivities of an overloaded line to injections at all the buses
In the below equation, how to quickly get these values?
  A useful reference is O. Alsac, J. Bright, M. Prais, B. Stott, “Further Developments in LP-Based Optimal Power Flow,” IEEE. Trans. on Power Systems, August 1990, pp. 697-711; especially see equation 3.

## Slide 27: Sensitivity Example in PowerWorld
Open case B5_DistFact and then Select Tools, Sensitivities, Flow and Voltage Sensitivities
  Select Single Meter, Multiple Transfers, Buses page
  Select the Device Type (Line/XFMR), Flow Type (MW), then select the line (from Bus 2 to Bus 3)
  Click Calculate Sensitivities; this shows impact of a single injection going to the slack bus (Bus 1)
  For our example of a transfer from 2 to 3 the value is the result we get for bus 2 (0.5440) minus the result for bus 3 (-0.1808) = 0.7248
  With a flow of 118 MW, we would hit the 150 MW limit with (150-118)/0.7248 =44.1MW, close to the limit we found of 45MW

## Slide 28: Sensitivity Example in PowerWorld
If we change the conditions to the anticipated maximum loading (changing the load at 2 from 118 to 118+44=162 MW) and we re-evaluate the sensitivity we note it has changed little (from -0.7248 to -0.7241)
  Hence a linear approximation (at least for this scenario) could be justified
With what we know so far, to handle the contingency situation, we would have to simulate the contingency, and reevaluate the sensitivity values
  We’ll be developing a quicker (but more approximate) approach next