## Slide 1: ECE 530 – Analysis Techniques for Large-Scale Electrical Systems
Prof. Hao Zhu
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
haozhu@illinois.edu
10/26/2015
Lecture 15: Flow Sensitivity Analysis

## Slide 2: Sensitivity Analysis
System description and notation
Motivation for the sensitivity analysis
Derivations of (linearized) flow sensitivity
Definitions of the various distribution factors
Analysis of the distribution factors
Distribution factor applications

## Slide 3: Problem Formulation
Find how sensitive line flows are to real power injections
Denote the system state by
Denote the conditions corresponding to the existing commitment/dispatch by x(0), p(0) and f(0) so that
the power flow equations
line active power flow vector
with

## Slide 4: Power Balance Equations
where
constant

## Slide 5: First-order Approximation
For a small change, p, that moves the injection from p(0) to p(0) + p , we have a corresponding change in the state x satisfying
We apply a first-order Taylor’s series expansion as

## Slide 6: First-order Approximation
We consider this to be a “small signal” change, so we can neglect the h.o.t. in the expansion
Hence, in order to satisfy the power balance equations with this perturbation, it follows that

## Slide 7: Jacobian Matrix
Also, using the nonlinear power flow equations, we obtain
and then the power flow Jacobian

## Slide 8: Flow Sensitivity Matrix
With the standard assumption that the power flow Jacobian is nonsingular, then
We can then compute the change in the line real power flow vector
the flow sensitivity matrix

## Slide 9: Sensitivity Comments
Sensitivities can easily be calculated even for large systems
  If p is sparse (just a few injections) then we can use a fast forward; if sensitivities on a subset of lines are desired we could use a fast backward
Sensitivities are dependent upon the operating point
  Also they include the impact of marginal losses
Sensitivities could easily be expanded to include additional variables in x (such as phase shifter angle), or additional equations, such as reactive power flow

## Slide 10: Sensitivity Comments, cont.
Sensitivities are used in the optimal power flow; in that context a common application is to determine the sensitivities of an overloaded line to injections at all the buses
In the below equation, how to quickly get these values?
  A useful reference is O. Alsac, J. Bright, M. Prais, B. Stott, “Further Developments in LP-Based Optimal Power Flow,” IEEE. Trans. on Power Systems, August 1990, pp. 697-711; especially see equation 3.

## Slide 11: Sensitivity Example in PowerWorld
Open case B5_DistFact and then Select Tools, Sensitivities, Flow and Voltage Sensitivities
  Select Single Meter, Multiple Transfers, Buses page
  Select the Device Type (Line/XFMR), Flow Type (MW), then select the line (from Bus 2 to Bus 3)
  Click Calculate Sensitivities; this shows impact of a single injection going to the slack bus (Bus 1)
  For our example of a transfer from 2 to 3 the value is the result we get for bus 2 (0.5440) minus the result for bus 3 (-0.1808) = 0.7248

## Slide 12: Sensitivity Example in PowerWorld
If we change the conditions to the anticipated maximum loading (changing the load at 2 from 118 to 118+44=162 MW) and we re-evaluate the sensitivity we note it has changed little (from -0.7248 to -0.7241)
  Hence a linear approximation (at least for this scenario) could be justified
With what we know so far, to handle the contingency situation, we would have to simulate the contingency, and reevaluate the sensitivity values
  We’ll be developing a quicker (but more approximate) approach next

## Slide 13: Linearized Sensitivity Analysis
As the sensitivity matrix explicitly depends on x(0) and p(0), its computation is less than practical for large-scale power system applications
To simplify the computation of the sensitivity matrix, we adopt a linearized approximation approach
Recall the fast decoupled power flow assumptions

## Slide 14: Linearized Approximation
By using the approximations from the FDPF we can get sensitivity values that are independent of the current state. That is, by using the B' and B" matrices
We can also linearize line flow equation

## Slide 15: Linearized Approximation
Hence, for each line
and thus,
(the negative sign goes away because )
T
T
T

## Slide 16: Matrix Definitions
Recall the series admittance of line is , and we define the matrix
We define the LN incidence matrix:
where the element j of vector ai is nonzero , whenever line is coincident with bus j.

## Slide 17: Linearized Real Power Flow
Under these assumptions the change in the line real power flows are given as
The constant flow sensitivity matrix
is termed as the injection shift factor (ISF) matrix.

## Slide 18: Injection Shift Factors (ISFs)
The -th element of ,is called the ISF of line l with respect to the injection at bus n
  Absorbed at the slack bus, so it is slack bus dependent
The terms generation shift factor (GSF) and load shift factor (LSF) can be similarly defined
  Same concept, just a variation in the sign whether it is a generator or a load
  Sometimes the associated element is not a single line, but rather a combination of lines (an interface)
Terminology used in North America are given in the NERC glossary (http://www.nerc.com/files/glossary_of_terms.pdf)

## Slide 19: ISF : Interpretation
is the fraction of the additional 1 MW injection at node n that goes though line l
slack
bus

## Slide 20: ISF : Properties
By definition, depends on the location of the slack bus
By definition, for since the injection and withdrawal buses are identical in this case and, consequently, no flow arises on any line l
The magnitude of is at most 1, that is,
Note, this is strictly true only for the linear (lossless) case. In the nonlinear case, it is possible that a transaction decreases losses so a 1 MW injection changes a line flow by more than 1 MW.

## Slide 21: Five Bus Example: Base Case

## Slide 22: Five Bus ISF, Line 4, Bus 2 (to Slack)

## Slide 23: Five Bus Example
The rows of A correspond to the lines and transformers, the columns correspond to the non-slack buses (buses 2 to 5); for each line there is a 1 at one end, a -1 at the other end (hence an assumed sign convention!).
Here we put a 1 for the lower numbered bus
~

## Slide 24: Five Bus Example

## Slide 25: Five Bus Example Comments
At first glance, the numerically determined value of (128-118)/20=0.5 does not match closely with the analytic value of 0.5455; however, in doing the subtraction we have lost some numeric accuracy
  Adding more digits helps (128.40 – 117.55)/20 = 0.5425
The previous matrix derivation isn’t intended for actual computation; is a full matrix so we would seldom compute all of its values
Sparse vector methods can be used if we are only interested in the ISFs for certain lines and certain buses