## Slide 1: ECE 530 – Analysis Techniques for Large-Scale Electrical Systems
Prof. Hao Zhu
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
haozhu@illinois.edu
11/2/2015
Lecture 17: Distribution Factors
and Applications

## Slide 2: Announcements
Homework 5 posted, due Nov 11
Final exam scheduled for the afternoon of Dec. 14

## Slide 3: Sensitivity Analysis
System description and notation
Motivation for the sensitivity analysis
Derivations of (linearized) flow sensitivity
Definitions of the various distribution factors
Analysis of the distribution factors
Distribution factor applications

## Slide 4: Distribution Factors
Various additional distribution factors may be defined
  power transfer distribution factor (PTDF)
  line outage distribution factor (LODF)
  line closure distribution factor (LCDF)
  outage transfer distribution factor (OTDF)
These factors may be derived from the ISFs making judicious use of the superposition principle

## Slide 5: PTDF Evaluation

## Slide 6: LODFs
outaged
base case
outage case
A good reference is Power Generation, Operation and Control by Wood and Wollenberg; there is now a 3rd edition

## Slide 7: LODF Evaluation
We select tk to be such that
As the transaction w' results in a flow on line k of
it follows that

## Slide 8: LODF Evaluation
For the rest of the network, the impacts of the outage of line k are the same as the impacts of the additional basic transaction wk
Therefore, by definition

## Slide 9: Developing a Critical Eye
In looking at the below formula we need to think about what conditions will cause this formula to fail
Here an obvious case is when the denominator is zero
That corresponds to a situation in which the contingency causes system islanding
  An example is line 6 (between buses 4 and 5)
  Impact modeled by injections at the buses within each viable island

## Slide 10: Calculating LODFs in PowerWorld
Select Tools, Sensitivities, Line Outage Distribution Factors
  Select the Line using dialogs on right, and click Calculate LODFS; below example shows values for line 4

## Slide 11: Multiple Line LODFs
LODFs can also be used to represent multiple device contingencies, but it is usually more involved than just adding the effects of the single device LODFs
Assume a simultaneous outage of lines k1 and k2
Now set up two transactions, wk1 (with value tk1) and wk2 (with value tk2) so

## Slide 12: Multiple Line LODFs
Substituting into PTDFs
Equation for the change in flow on line l for the outage of lines k1 and k2 is

## Slide 13: Multiple Line LODFs
Example: Five bus case, outage of lines 2 and 5 to flow on line 4.

## Slide 14: Multiple Line LODFs
Flow goes from 117.5 to 118.0

## Slide 15: Line Closure Distribution Factors (LCDFs)
The line closure distribution factor (LCDF), LCDFl,k, for the closure of line k (or its addition if it does not already exist) is the portion of the line active power flow on line k that is distributed to line l due to the closure of line k
Since line k is currently open, the obvious question is, “what flow on line k?”
Answer (in dc sense) is the flow that will occur when the line is closed (which we do not know before closure)

## Slide 16: Line Closure Distribution Factors
Closed line
base case
line k addition case

## Slide 17: LCDF : Evaluation
We can evaluate LCDF by reversing the line outage
Recall how we define LODF
outaged
base case
outage case

## Slide 18: LCDF : Evaluation
So the post-outage line flow in LCDF is exactly the pre-outage line k flow in LODF
But the change in line l flow in LCDF becomes the opposite of that in LODF
So for the LCDF calculation
Hence, we have

## Slide 19: Outage Transfer Distribution Factor
The outage transfer distribution factor (OTDF) is defined as the PTDF with the line k outaged
The OTDF applies only to the post-contingency configuration of the system since its evaluation explicitly considers the line k outage
This is a quite important value since power system operation is usually contingency constrained

## Slide 20: Outage Transfer Distribution Factor
outaged
line
=

## Slide 21: OTDF : Evaluation
=
+

## Slide 22: OTDF : Evaluation
Since
and
then so that

## Slide 23: Five Bus Example
Say we would like to know the PTDF on line 1 for a transaction between buses 2 and 3 with line 2 out

## Slide 24: Five Bus Example
Hence we want to calculate these values without having to explicitly outage line 2
The value we are looking for
is 0.2 (20%)

## Slide 25: Five Bus Example
Evaluating: the PTDF for the bus 2 to 3 transaction on line 1 is 0.2727; it is 0.1818 on line 2 (from buses 1 to 3); the LODF is on line 1 for the outage of line 2 is -0.4
Hence
For line 4 (buses 2 to 3) the value is

## Slide 26: UTC Revisited
We can now revisit the uncommitted transfer capability (UTC) calculation using PTDFs and LODFs
Recall trying to determine maximum transfer between two areas (or buses in our example)
For base case maximums are quickly determined with PTDFs

## Slide 27: UTC Revisited
For the contingencies we use
Then as before

## Slide 28: Five Bus Example

## Slide 29: Five Bus Example
Therefore, for the base case

## Slide 30: Five Bus Example
For the contingency case corresponding to the outage of the line 2 The limiting value is line 4
Hence the UTC is limited by the contingency to 23.0

## Slide 31: Contingency Considerations
Traditionally contingencies consisted of single element failures (N-1), though utilities have long considered multiple element contingencies
  Some can be quite complex
N-2 involves considering all double element contingencies
N-1-1 is used to describe contingencies in which a single element contingency occurs, the system is re-dispatched, then a second contingency occurs
  The number of contingencies considered following the first contingency can be quite large, coming close to N-2

## Slide 32: Additional Comments
Distribution factors are defined as small signal sensitivities, but in practice, they are also used for simulating large disturbance cases
Distribution factors are widely applied in the operation of electricity markets where the rapid evaluation of the impacts of each transaction on the line flows is required
Applications to actual system show that the distribution factors provide satisfactory results in terms of accuracy
For multiple applications that require fast turn around time, distribution factors are used very widely, particularly, in the market environment