## Slide 1: ECE 333 Green Electric Energy
Lecture 14: Wind Energy Conversion Systems (WECS)
Dr. Karl Reinhard
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
reinhrd2@illinois.edu

## Slide 2: Announcements
Continue Reading Chapter 7
HW 8 is posted on the website;
Quiz 8 on 5 April
Midterm 2 on 12 April (during class);
  Closed book, closed notes;
  Bring standard calculator
  One 8.5 by 11 inch note sheet that you have prepared

## Slide 3: Types of Wind Turbines
“Windmills” are used to grind grain into flour
Many “Wind Turbine” names –
  wind-driven generator
  wind generator
  wind turbine
  wind-turbine generator (WTG)
  wind energy conversion system (WECS)”
Wind turbines characterized by turbine blade’s axis of rotation
  Horizontal axis wind turbines (HAWT)
  Vertical axis wind turbines (VAWT)
Groups of wind turbines are located in what is called either a “wind farm” or a “wind park”
Notes: 2

## Slide 4: Typical Wind Energy Conversion System Components
  FIGURE 7.5 Principal components of most wind energy conversion systems.
    Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.
Notes: 3

## Slide 5: Turbine Blade – an Air Foil
  FIGURE 7.7 (a) Lift in wing (b) wind turbine blade forces
  Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.
  FIGURE 7.8 Increasing the angle of attack can cause a wing to stall
  Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.
Notes: 4

## Slide 6
H. Kim and D. Lu, "Wind Energy Conversion System from Electrical Perspective—A Survey," Smart Grid and Renewable Energy, Vol. 1 No. 3, 2010, pp. 119-131. doi: 10.4236/sgre.2010.13017.
https://www.popsci.com/technology/article/2010-03/next-gen-wind-turbine
Wind Energy Conversion Systems

## Slide 7: Vertical Axis Wind Turbines
Darrieus rotor - the only commercially successful vertical axis machine
Wind flowing by the vertical blades (aerofoils) generates “force” producing rotation
No yaw (rotation about vertical axis) control needed to keep them facing into the wind
Heavy machinery in the nacelle is located on the ground
Blades are closer to ground where wind-speeds are lower
Notes: 6

## Slide 8: Horizontal Axis Wind Turbines (HAWT)
“Downwind” HAWT – turbine blades are downwind of the tower
Advantage: No yaw control needed –blades naturally orient to wind direction
Disadvantages: Tower disrupts the air stream causing turbulence
  vibration
  mech stress on the blade and supporting structure
Notes: 7

## Slide 9: Horizontal Axis Wind Turbines (HAWT)
“Upwind” HAWT – blades face into the wind
Most modern wind turbines are “upwind” configuration
Advantages:
  Significantly reduced vibrations… and mechanical stress ($ savings)
  deliver more power ($)
Disadvantage: Requires somewhat complex yaw control to maintain orientation facing into the wind
Notes: 8

## Slide 10: Number of Rotating Blades
Windmills have multiple blades
  high starting torque needed to overcome pumping rod weight / inertia
  low windspeeds required to provide nearly continuous water pumping
  comparatively larger rotor area faces the wind
Turbines with many blades operate at much lower rotational speeds - as the speed increases, the turbulence caused by one blade impacts the other blades
Most modern wind turbines have two or three blades
http://pixelpops.com/public_photos/what.html
Notes: 9

## Slide 11
Classifying Wind Energy Conversion Systems
Rotation Speed
Fixed-speed turbines
Variable Speed turbines
  Indirect drive (w/gear box)
  Direct drive (w/o gear box)
Power Electronics – Wind Generation System w/
No power converter
Partial-capacity power converter
Full-capacity power converter

## Slide 12: Wind Energy Conversion Systems
    FIGURE 7.9 System configurations for wind energy systems.
    Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.
Notes: 11

## Slide 13
Machine Conditions: Elect-Mech Power Conversion
Adapted from Fig 4.1.6, H. H. Woodson and J. R. Melcher, Electromechanical Dynamics Part I: Discrete Systems, John Wiley & Sons, Inc., New York, 1968.
A general machine is excited by ideal sources

## Slide 14
Machine Conditions for Average Power Conversion
Adapted from Fig 4-34, A. E. Fitzgerald, C. Kingsley, and S. D. Umans, Electric Machinery, 5th ed, McGraw-Hill Book Co., New York, 1990.
Instantaneous power
Substitution

## Slide 15
Machine Conditions for Average Power Conversion
Adapted from Fig 4-34, A. E. Fitzgerald, C. Kingsley, and S. D. Umans, Electric Machinery, 5th ed, McGraw-Hill Book Co., New York, 1990.
Trig manipulation 
Because a sinusoidal time function has no average value, when a coefficient of

## Slide 16
Machine Conditions for Average Power Conversion
 A key element of machine theory is satisfying the frequency condition with the available electrical & mechanical sources to match machine characteristics with the application
Hence 4 frequency conditions for average power conversion can
be compactly written

## Slide 17: Synchronous Machines
Spin at a fixed rotational speed ( determined by the number of poles and by the frequency, e.g.
  3600 rpm @ 60Hz, 2 pole
  1800 rpm @ 60Hz, 4 pole (explained next slide)
The stator magnetic field matches system frequency ()
Create the rotor magnetic field w/ direct current (= 0) on the rotor windings
  Slip rings are needed to make the dc current connection on the rotor
  Permanent magnets are an alternative
A gear box often needed between the blades and the generator
  Some newer machines are designed without a gear box

## Slide 18: Magnetic Poles
Synchronous speed depends on the electrical frequency and the number of poles, with
Image source :cnx.org/contents/cbb3bd3b-430a-487b-9c53-b17d79e3367c@1/Chapter_5:_Synchronous_Machine

## Slide 19: Asynchronous Induction Machines
Spins at a variable speed ()
Acts as a motor during start up; can act as a generator when spun faster then synchronous speed
Does not require exciter, brushes, and slip rings
  Less expensive
  Require less maintenance
The magnetic field is created on the stator not the rotor
Current is induced in the rotor (Faraday's law: v= dl/dt)
Lorenz force on wire with current in magnetic field:

## Slide 20: Squirrel-Cage Induction Generator
    FIGURE 7.11 Cage Conductor Force & Current
    Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.
    FIGURE 7.10 Squirrel-Cage Induction Generator
    Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.
Notes: 19

## Slide 21: The Inductance Machine as a Motor
Rotating stator magnetic field causes rotor to spin in the same direction
As rotor approaches , the relative motion becomes less and less
If , no relative motion, I = 0, and no force
Thus in an induction motor
Fig 7-13, A. E. Fitzgerald, C. Kingsley, and S. D. Umans, Electric Machinery, 5th ed, McGraw-Hill Book Co., New York, 1990.

## Slide 22: Slip
Slip captures the difference between the stator and the rotor speeds
s = rotor slip – positive for a motor, negative for a generator
  NS = no-load synchronous speed (rpm)
  f = frequency (Hz)
  P = number of poles
  NR = rotor speed (rpm)

## Slide 23: The Induction Machine as a Generator
External mechanical force causes rotation exceeding electrical speed ()
Slip becomes negative
Power transferred from mechanical to electrical
Fig 7-13, A. E. Fitzgerald, C. Kingsley, and S. D. Umans, Electric Machinery, 5th ed, McGraw-Hill Book Co., New York, 1990.

## Slide 24: The Induction Machine as a Generator
The stator requires excitation current
  from the grid if it is grid-connected or
  by incorporating external capacitors
Single-phase, self-excited, induction generator
Wind speed forces generator shaft to exceed synchronous speed

## Slide 25: The Induction Machine as a Generator
Slip is negative because the rotor spins faster than synchronous speed
Slip is normally less than 1% for grid-connected generator
Typical rotor speed

## Slide 26: Speed Control
Necessary to be able to shed wind in high-speed winds
Rotor efficiency changes for different Tip-Speed Ratios (TSR), and TSR is a function of windspeed
To maintain a constant TSR, blade speed should change as wind speed changes
A challenge is to design machines that can accommodate variable rotor speed and fixed generator speed

## Slide 27: Blade Efficiency vs. Windspeed
At lower windspeeds, the best efficiency is achieved at a lower rotational speed

## Slide 28: Indirect Grid Connection Systems
Wind turbine is allowed to spin at any speed
Variable frequency AC from the generator goes through a rectifier (AC-DC) and an inverter (DC-AC) to 60 Hz for grid-connection
Good for handling rapidly changing windspeeds

## Slide 29: Wind Turbine Gearboxes
A significant portion of the weight in the nacelle is due to the gearbox
  Needed to change the slow blade shaft speed into the higher speed needed for the electric machine
Gearboxes require periodic maintenance (e.g., change the oil), and have also be a common source of wind turbine failure
Some wind turbine designs are now getting rid of the gearbox by using electric generators with many pole pairs (direct-drive systems)

## Slide 30: Doubly-fed Induction Generator (DFIG)
    FIGURE 7.12 A wound-rotor, doubly-fed induction generator (DFIG)
    Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.
Notes: 29

## Slide 31: Gearless Variable-Speed Synchronous Generator
    FIGURE 7.13 A gearless variable-speed synchronous generator.
    Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.
Notes: 30

## Slide 32: Types of Wind Turbines by Machine
From an electric point of view there are four main types of large-scale wind turbines (IEEE naming convention)
  Type 1: Induction generator with fixed rotor resistance
  Type 2: Induction generators with variable rotor resistance
  Type 3: Doubly-fed induction generators
  Type 4: Full converter generators which main use either a synchronous generator or an induction generator
Most new wind turbines are either Type 3 or Type 4
In Europe these are sometimes called Types A, B, C, D respectively.

## Slide 33: IEEE Type 1 (Induction w/ Fixed Rotor R)
Induction generator connected with a fixed rotor resistance
Design requires additional components for grid connection:
  Soft-starter to decrease current transients during startup phase
  Capacitor bank to compensate for reactive power.
Capacitor bank enables the generator can work close to 0 value generation and 0 reactive power consumption.
This compensation approach does not provide flexible reactive power control
Notes: 32

## Slide 34: IEEE Type 2 (Induction w/ Variable Rotor R)
Type B WECS generator is designed to work with limited variable speed wind turbine
Variable resistor in the machine rotor, enables controlled-power output
Capacitor bank and soft-starter are analogous to the type A design
Notes: 33

## Slide 35: IEEE Type 3 (Doubly-fed Induction Generator)
WECS control enabled by two AC/DC converters w/ a connecting capacitor
Wound rotor induction generator – known as a doubly fed induction generator (DFIG)
“Doubly” as the rotor winding is not short-circuited (as in classical “singly-fed” induction machine); voltage is induced from the rotor-side converter
2 operating schemes: constant (1) reactive power or (2) voltage
Most commonly installed WECS
Notes: 34

## Slide 36
Type D design includes full-scale frequency converter with different generator types.
Most common – permanent magnet synchronous generator (PMSG).
This design enables
full active / reactive power production control
high wind energy extraction value
Full power control improves power and frequency stability and reduces the short circuit power.
Most type D designs do not need a gearbox – a distinct advantage
IEEE Type 4 (Var. Speed w/ Full Pwr Elect Conv.)
Notes: 35

## Slide 37
F. Iov and F. Blaabjerg, "Power electronics and control for wind power systems," 2009 IEEE Power Electronics and Machines in Wind Applications, Lincoln, NE, 2009, pp. 1-16. doi: 10.1109/PEMWA.2009.5208339
Another Classification Taxonomy

## Slide 38: Announcements
No Homework / Quiz this week
Homework 7 Posted
Quiz 7 Thursday after Spring Break
Reading Chapter 7
Thanks to EOH Volunteers – GREAT SUCCCESS
Spring Break Safety !!