## Slide 1: ECE 333 Green Electric Energy
Hydro and Wave Power
Dr. Karl Reinhard
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
reinhrd2@illinois.edu

## Slide 2: Announcements
Reading Chapter 8 – More Renewable Energy Systems
  Wave energy conversion
  Hydroelectric
  Pumped-storage Hydro
HW 9 will be covered during an in-class Quiz 9 on 19April
Final Exam is Tuesday 8 May, 8 to 11 am

## Slide 3: Types of Hydro
Diversion (also known as run-of-river)
  Some of the water is channeled into a canal or penstock and through the turbine
  It will tend to have little or no storage; the energy associated with water that is not diverted is lost
  Because there is no need to build a dam, diversion hydro often has less environment impact
Image: http://energy.gov/eere/water/types-hydropower-plants

## Slide 4: Types of Hydro
Pumped Storage
  Uses the potential energy of water to "store" electricity
  Part of the time it works as a conventional impoundment hydro plant with water in a high reservoir flowing through the turbine to a lower reservoir (or lake/river)
  Part of the time it functions as a large load as water is pumped from the lower reservoir back to the higher reservoir
  Works as a generator when the price of electricity is high (e.g., during the day) and as a load when price of electricity is low (e.g., during the night)
  Round trip efficiency can be up to 80%

## Slide 5: Hydro Power – 2006 (Most Widely Used Renewable Resource)
Hydro power is the most widely used renewable resource in the world.
U.S. 2.9 quad (billions of kWh);
  ~ 3% of total energy,
  ~ 9% of total electricity.
Worldwide hydro (2006) (billion kWhs, % energy demand):
  Canada (352, 59%),
  Brazil (345, 84%),
  Norway (118, 98%),
  China (431, 16%),
  South America is about 2/3 hydro (639.6/951.0)
  Worldwide (2998, 16.6%)
http://www.eia.doe.gov/emeu/international/RecentElectricityGenerationByType.xls
Notes: 4

## Slide 6: Largest Hydro US: Grand Coulee, WA
Largest hydro power station is US is on the Columbia River in Washington State. It was opened in 1942, and now has a total capacity of 6.8 GW
  Hydraulic head is 380 feet; reservoir size is 125 sq miles
http://en.wikipedia.org/wiki/Grand_Coulee_Dam
Notes: 5

## Slide 7: Lighting Africa, Grand Inga, DR Congo
Africa’s 2006 Total electric consumption was 547 TWh,
(less than Canada’s 594 TWh)
South Africa (228 TWh) and Egypt (109 TWh)
 257 TWh for 800M remaining people, a value of
~ 321 kWh per capita,  37 watts average consumption
  Note, this value includes industrial, commercial and residential consumption
  Total electric capacity in Africa (excepting South Africa and Egypt) is less than 60 GW, about 1/3 of which is hydro
  Yet Africa has hydro electric capacity of 100’s of GW
Notes: 6

## Slide 8: Lighting Africa: Grand Inga, DR Congo
Hydro at the Inga dams in Congo (on Congo River)
  1.8 GW current capacity,
  >> 40 GW potential capacity, w/ 370 TWh annual energy production !
Notes: 7

## Slide 9: Pumped Storage Example
Total installed U.S. capacity ~ 16,500 MW
http://www.hydroworld.com/content/dam/etc/medialib/new-lib/hydroreview/print-articles/volume-30/issue-2/48198.res/_jcr_content/renditions/pennwell.web.450.311.gif
http://www.ferc.gov/industries/hydropower/gen-info/licensing/pump-storage/diagram-pump.asp
Example: Raccoon Mountain – 650 MW
  stores ~ 20 hours of water flow;
  fills in 28 hours;
  water levels change 100 ft

## Slide 10: Useful Conversions for Water
 | American | SI
1 ft3 | 7.4805 gal | 0.02832 m3
1 ft/ second | 0.6818 mph | 0.3048 m/s
1 ft3/second | 448.8 gpm | 0.02832 m3/s
Water density | 62.428 lb/ft3 | 1000 kg/m3
1 psi | 2.307 ft of water | 6896 N/m2
1 kW | 737.56 ft-lb/s | 1000 N-m/s
Use this to find the potential power available given a head HN and a flow rate Q
Water has potential energy (mgh), kinetic energy (½mv2) and pressure energy (mgh → noncompressible)
Note, pounds is a unit of force; 1 slug = 14.6 kg (32.2 lbs at one g)

## Slide 11: Micro Hydro (less than 100 kW)
    FIGURE 8.30 A micro-hydropower system in which water is diverted into a penstock and delivered to a powerhouse below.
    Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.
Notes: 10

## Slide 12
    FIGURE 8.31 Transformations of energy in a hydroelectric system.
    Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.

## Slide 13
    Fig. 8.31 Transformation of Energy in a hydroelectric system.
    Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.
    Table. 8.10 Useful Conversions for Water
    Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.

## Slide 14: Pipe Head Loss
    FIGURE 8.34 Net head is what remains after pipe losses are accounted for.
    Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.
Notes: 13

## Slide 15: Head Loss from Pipes
    FIGURE 8.35 Friction head loss, in feet of head per 100 ft of pipe, for 160-psi PVC piping and for polyethylene, SDR pressure-rated pipe.
    Masters, Gilbert M. Renewable and Efficient Electric Power Systems, 2nd Edition. Wiley-Blackwell, 21/06/2013.
Notes: 14

## Slide 16: Water Tower Example
How much energy is in a 500,000 gallon water tower with an average height of 200 ft (60.9 m)?
Mass of water
Energy
250,000 gallons in the Philo, IL tower

## Slide 17: Water Tower Example, cont’d
What is the equivalent pressure head?
specific weight of water
Specific weight units are either lb/ft3 or N/m3

## Slide 18: Micro Hydro Setup
At top- gross head (HG) = z [feet]
At bottom- net head (HN)
Losses- HL=HG-HN [feet]
Potential Energy
Pressure
Kinetic Energy
z
Reservoir
Penstock
Turbine

## Slide 19: Pipe Losses
A 4’’ pipe delivers 150 gallons/minute (gpm) through an elevation change of 100 ft. Pressure at pump house is 27 psi. What are pipe losses?
Total head is 62.51 ft
Head loss: 100 – 62.5 = 37.49 ft

## Slide 20: Power Theoretically Available
Need to convert units to get power in kW
Since the conversion factors are always the same, we can simplify to
The dependence of on Q and H is the same regardless of whether high flow, low height or low flow, high height

## Slide 21: Hazen-Williams Loss Equation
Empirical frictional head loss calculation
Q = flow rate [gal/min]
L = length of pipe [ft]
D = diameter of pipe [in]
C = roughness coefficient (PVC = 150; corrugated steel = 60; smooth steel, cement = 130 to 140)
Book approximation for fixed pipe size:

## Slide 22: Salt Fork River Example
How much power is in the Salt Fork River?
  100 ft3/sec, 7.48 gal/ft3, 3.78 liter/gallon
Equivalent head:
Note, the real-time flow for the Salt Fork (at St. Joseph) is available at http://waterdata.usgs.gov/nwis/uv?03336900
4/17/18 Flow rate was ~ 361 cubic feet/second; max is about 9000 cubic feet/second.
Congo is 1.5 million cubic feet per second while Amazon can reach 11 million cubic feet per second! Grand Inga power estimate = (1.5e6*60*7.48*450)/5.3 = 57GW
Assuming 1 m/s velocity

## Slide 23: Homer Lake Hydro Example
80 acres, 30 ft head, say we get 4488 gal/minute out, and capacity factor is 100%
What is power/energy impact for 100 ft of 10” vs. 12” pipe?
10”
Efficiency η is 50%:
Capacity factor is 100%:
image: http://www.ccfpd.org/about/Map_HL_final_vert_042010.pdf
Hazen-Williams Loss Equation

## Slide 24: Homer Lake Hydro Example
Assume an efficiency η of 50% and a capacity factor of 100%
12”
http://www.ccfpd.org/about/Map_HL_final_vert_042010.pdf

## Slide 25: Optimal Flow Rate
Suppose the pipe diameter is fixed
However, a larger diameter will always lower losses
Theoretical maximum flow and therefore power is delivered by a pipe when losses are equal to 1/3 of the gross head
Q (gpm)
P(W)
low loss, low P
high loss, low P
(optimal)

## Slide 26: Turbine Design - 3 Approaches
1. Impulse turbines
- most common for micro-hydro systems
- capture kinetic energy of high-speed jets
- high head, low flow
2. Reaction turbines
- pressure difference of blades creates a torque
- low head, high flow
3. Waterwheel
-slow-moving but powerful
- converts potential energy to mechanical energy

## Slide 27: Impulse Turbine Example: Pelton Wheel
The original impulse turbine by Lester Pelton in 1870's
Water flows from nozzles onto sets of buckets attached to the rotating wheel
Uses velocity of water, with no down side suction

## Slide 28: Reaction Turbines
Develops power from combined action of the pressure and moving water
Placed directly in the stream of flowing water; better for locations with low head and high flow
Examples: Francis Turbine, invented by James Francis in 1848
Image at left shows example from Three Gorges
http://en.wikipedia.org/wiki/Francis_turbine#/media/File:Sanxia_Runner04_300.jpg
Full output in 2012; 98.8 TWh in 2014; US total 259 TWh

## Slide 29: Waterwheels
Not very efficient, but can be considered for micro hydro situations in which the head is low
Relatively simple to install
Often viewed as aesthetically pleasing
http://www.british-hydro.org/waterwheels.html

## Slide 30: Wave Power
The potential energy available waves is quite high, with some estimates up to 2 TW (2000 GW) worldwide.
The potential wave power per meter varies with the square of the wave height and linearly with the period
  Three meter waves with an 8 second period produces about 70.5 kW/m, while 15 meter waves with a 15 second period produces about 3.3 MW/m
Density of sea water, r, is 1025 kg/m3 (give or take);
g (gravity) is 9.8 m/s2 ;
H is wave trough-crest height; and
T is period

## Slide 31: Wave Power
Waves are more complex, consisting of a number of superimposed frequencies
A common way to estimate power is to just count the heights of the highest 1/3 of the waves, H1/3

## Slide 32: Significant Wave Height
The significant wave height, Hs, assumes a Rayleigh statistical distribution on the wave heights
Then Tp is associated with an assumed distribution of the wave periods
Then the power is
Hs and Tp data is available for many locations
Image source: http://upload.wikimedia.org/wikipedia/commons/8/87/Wavestats.svg

## Slide 33: Annual Average Wave Power (kW/m)
Source://www.energy.ca.gov/2006publications/CEC-500-2006-119/CEC-500-2006-119-D.PDF

## Slide 34: There Can Be Significant Seasonal Variation
Figure shows data for a site by Oregon; just like for other energy sources, capacity factors come into play
http://oceanenergy.epri.com/attachments/wave/reports/Ph_15_Oregon_Wave_Final_RB_121305.pdf
CF values tend to be no more than 30%

## Slide 35: Wave Energy Conversion Technologies
Industry is in infancy, so different technologies are being considered
  More than 1000 have been patented!
Creating durable, economic devices is challenging!
Design is partially driven by location
  Close to shore: easier to maintain, close to utility, waves coming in fixed direction, smaller waves so conditions less extreme; but wave power is less; tidal issues could also be a concern
  Offshore are in deeper water and subject to more extreme conditions; but wave power is higher and tidal issues are less; wave directions more variable

## Slide 36: Wave Energy Conversion Technologies
Major design technologies
  (1) Point absorber buoy: buoy goes up and down to drive pumps to generate electricity
  (2) Surface attenuator: device flexes as waves go by, driving pumps that generate electricity
  (3) Oscillating wave surge: one end fixed, the other is free to move; energy collected from relative motion
Source: http://en.wikipedia.org/wiki/Wave_power

## Slide 37: Wave Energy Conversion Technologies
  (4) Oscillating water column: waves compress air, which is used to generate electricity
  (5) Overtopping device: wave velocity used to fill a reservoir, with energy captured by low head turbines
Source: http://en.wikipedia.org/wiki/Wave_power

## Slide 38: Wave Power
World’s largest wave park” was the Agucadoura Wave Farm in Portugal, with capacity of 2.25 MW
Each of three devices was 142m long, and has a diameter of 3.5 m, and uses 700 metric tons of steel
Surface attenuator design, using high pressure oil
Capacity factor seemed to be about 20%
In-service for less than one year (2008)

## Slide 39: Oyster 800 Wave Energy Machine
Device is 26 m in width, installed at a depth of 13 m, about 500 m from shore; can produce 800 kW
  Located by Orkney, Scotland, UK
Company (Aquamarine Power) claims three benefits: simplicity, survivability, and shore-based
Unit has operated for 20,000 hours; 70% of | energy is from October to March; overhaul during summer
http://www.aquamarinepower.com/projects/oyster-800-project-orkney/
https://www.youtube.com/watch?v=fCheEfaoCOs