## Slide 1: ECE 333 Green Energy Systems
Lecture 4: Three-Phase
Dr. Karl Reinhard
Dept. of Electrical and Computer Engineering
University of Illinois at Urbana-Champaign
reinhrd2@illinois.edu

## Slide 2: Announcements
Be reading Chapter 3 from the book
Quiz today on Homework 1
Homework 2 will be posted this afternoon.
Quiz on Thursday, 1 Feb

## Slide 3: Complex Power
Asterisk denotes complex conjugate
S
Apparent
(complex) power
P – Real Power
Heat, motion, etc.
Q – Reactive Power
Energy stored in Electric or Magnetic Field
S = P + jQ
S
Q
P
POWER TRIANGLE

## Slide 4: Apparent, Real, Reactive Power
P = Real power (W, kW, MW)
Q = Reactive power (VAR, kVAR, MVAR)
S = Apparent power (VA, kVA, MVA)
Power factor angle
Power factor

## Slide 5: Apparent, Real, Reactive Power
Remember ELI the ICE man
ELI
ICE
I lags V (or E)
I leads V (or E)
S
Q
P
P
Q
S
Q and f are negative
Q and f are positive
Inductive loads: + Q
Capacitive loads: – Q

## Slide 6: Apparent, Real, Reactive Power
Relationships between P, Q, and S can be derived from the power triangle just introduced
Ex: A 100 kW load with leading pf of 0.85. What are the f (power factor angle), Q (reactive power), and S (apparent power)?
P
Q
S
Q and f are negative
leading pf  Capacitive Load

## Slide 7: Conservation of Power
Kirchhoff’s voltage and current laws (KVL and KCL)
  Sum of voltage drops around a loop must be zero
  Sum of currents into a node must be zero
Conservation of power follows
  Sum of real power into every node must equal zero
  Sum of reactive power into every node must equal zero

## Slide 8: Conservation of Power Example
Resistor: consumed power
Inductor: consumed power
Q
P
S
Inductive load: + Q

## Slide 9: Power Consumption in Devices
Resistors only consume real power
Inductors only consume reactive power
Capacitors only produce reactive power

## Slide 10: Example
Solve for the apparent power delivered by the source

## Slide 11: Reactive Power Compensation
Reactive compensation is used extensively by utilities
Capacitors are used to correct the power factor (pf)
This allows reactive power to be supplied locally
Supplying reactive power locally decreases line current, which results in
  Decreased line losses
  Ability to use smaller wires
  Less voltage drop across the line

## Slide 12: Power Factor Correction Example
Assume we have a 100 kVA load with pf = 0.8 lagging, and would like to correct the pf to 0.95 lagging. How many kVAR?
We know:
We want:
S
Qdes.=?
P = 80
Thus requiring a capacitor producing kVar:
Q = 60
Qcap = -33.7
P = 80
Qdes= 26.3
P = 80
Notes: 11

## Slide 13: Balanced 3 Phase () Systems
A balanced 3 phase () system has
  3 voltage sources w/ equal magnitude, but w/ 120 phase shift
  Equal loads on each phase
  Equal impedance on the lines connecting generators to loads
Bulk power systems are almost exclusively 3
Single phase is used primarily only in low voltage, low power settings, such as residential and some commercial
Van
Vcn
Vbn
Vab
Vca
Vbc
Notes: 12

## Slide 14: Balanced 3 -- No Neutral Current
Notes: 13

## Slide 15: 3 Power Advantages
Can transmit more power for same amount of wire (2x 1f)
3 machines produce constant torque (balanced conditions)
3 machines use less material for same power rating
3 machines start more easily than 1 machines
Notes: 14

## Slide 16: 3 Power Advantages – Rotating Field
Notes: 15

## Slide 17: Three Phase Transmission Line
Notes: 16

## Slide 18: Three Phase - Wye Connection
There are two ways to connect 3 systems
  Wye (Y)
  Delta ()
Notes: 17

## Slide 19: Wye Connection Line Voltages
Van
Vcn
Vbn
Vab
Vca
Vbc
-Vbn
Line to line voltages are balanced
(α = 0 in this case)
(Vl-l )
Notes: 18

## Slide 20: Wye Connection, cont’d
voltage across device to be phase voltage
current through device to be phase current
voltage across lines to be the line voltage
current through lines to be line current
Notes: 19

## Slide 21: Delta Connection
Ica
Ic
Iab
Ibc
Ia
Ib
-Ica
Phase voltages = Line voltages
Iab
KCL using
Load Convention !!
Notes: 20

## Slide 22: Three Phase Example
Assume a -connected load is supplied from a 3, 13.8 kV(l-l) source w/ Z = 10020W
a
b
c
b
c
a
Van
Vcn
Vbn
Vab
Vca
Vbc
Notes: 21

## Slide 23: Three Phase Example, cont’d
Ica
Ic
Iab
Ibc
Ia
Ib
-Ica
Notes: 22

## Slide 24: Delta-Wye Transformation
To simplify balanced 3f systems analysis:
Van
Vcn
Vbn
Vab
Vca
Vbc
Notes: 23

## Slide 25: Per Phase Analysis
Per phase analysis enables balanced 3 system analysis w/ the same effort as a single phase system
Balanced 3 Theorem: For a balanced 3 system w/
  All loads and sources Y– connected
  Mutual Inductance between phases is neglected
Notes: 24

## Slide 26: Per Phase Analysis
Per phase analysis enables balanced 3 system analysis w/ the same effort as a single phase system
Balanced 3 Theorem: For a balanced 3 system w/
  All loads and sources Y– connected
  Mutual Inductance between phases is neglected
 Then
  All neutrals are at the same potential
  All phases are COMPLETELY decoupled
  All system values are the same sequence as sources.
  Sequence order we’ve been using (phase b lags phase a and phase c lags phase a) is known as “positive” sequence
  Later we’ll discuss negative and zero sequence systems.
Notes: 25

## Slide 27: Per Phase Analysis Procedure
Per phase analysis procedure
Convert all  load/sources to equivalent Y’s
Solve phase “a” independent of the other phases
Total system power S = 3 Va Ia*
If desired, phase “b” and “c” values can be determined by inspection (i.e., ±120° degree phase shifts)
If necessary, go back to original circuit to determine line-line values or internal  values.
Notes: 26

## Slide 28: Per Phase Example
Assume a 3, Y-connected generator with Van = 10 volts supplies a -connected load with Z = -j through a transmission line with impedance of j0.1 per phase. The load is also connected to a -connected generator with Va”b” = 10 through a second transmission line which also has an impedance of j0.1 per phase.
Find
1. The load voltage Va’b’
2. The total power supplied by each generator, SY and S
Notes: 27

## Slide 29: Per Phase Example, cont’d
Notes: 28

## Slide 30: Per Phase Example, cont’d
Notes: 29

## Slide 31: Per Phase Example, cont’d
Notes: 30

## Slide 32: Per Phase Example, cont’d
Notes: 31

## Slide 33: Transformers Overview
Power systems are characterized by many different voltage levels, ranging from 765 kV down to 240/120 volts.
Transformers are used to transfer power between different voltage levels.
The ability to inexpensively change voltage levels is a key advantage of ac systems over dc systems.
In 333 we just introduce the ideal transformer, with more details covered in 330 and 476.