## Slide 1
Advanced Interface Box
for Solar Panels
ECE445: Senior Design Lab
Team 10:
Maram Safi
Nikhil Mathew Sebastian
Sydney Li

## Slide 2
Introduction
Project Sponsor: Arijit Banerjee
60 Research Solar Panels on ECEB roof
  Not distributing power into the grid
  Not adequately monitored
Previously attempted in Fall 2019
  Ethernet Connection
  Not Scalable
ECE 445, Fall 2021
GRAINGER ENGINEERING

## Slide 3
Solution: Advanced Interface Box
Collectively display live data of solar panels on a single portal
Webpage allowing ECEB personnel to both access and configure data
Allow for future full-scale implementation to all 60 solar panels
ECE 445, Fall 2021
GRAINGER ENGINEERING

## Slide 4
High-Level Requirements
Record 3 key solar panel parameters at the interface level:
  Voltage (accurate to within 300 mV)
  Current (accurate to within 1.5%)
  Temperature (accurate within ± 0.5°C)
Wireless communication capability with interface box through remote external portal (“Research Hub”) for observation and configuration
Interface boxes should allow for Scalability - ability to communicate with and retrieve data from multiple panels
ECE 445, Fall 2021
GRAINGER ENGINEERING
Notes: Nikhil

## Slide 5
Block Diagram
ECE 445, Fall 2021
GRAINGER ENGINEERING
Notes: Nikhil

## Slide 6
Initial PCB Design
ECE 445, Fall 2021
GRAINGER ENGINEERING

## Slide 7
Final PCB Design
ECE 445, Fall 2021
GRAINGER ENGINEERING

## Slide 8
Final PCB Design
ECE 445, Fall 2021
GRAINGER ENGINEERING

## Slide 9
Power
Subsystem
ECE 445, Fall 2021
GRAINGER ENGINEERING

## Slide 10
ECE 445, Fall 2021
GRAINGER ENGINEERING
Design Details

## Slide 11
The 12-volt power rail provides a 12-volt DC output within the range of ± 1%
Converts a 12-volt input into a 5-volt DC output within the range of 4.90V ≤ Vout ≤ 5.10V
Converts a 12-volt input into a 3.3-volt DC output within the range of 3.235V ≤ Vout ≤ 3.365V
ECE 445, Fall 2021
GRAINGER ENGINEERING
Requirements and Functional Tests

## Slide 12
Microcontroller
Subsystem
ECE 445, Fall 2021
GRAINGER ENGINEERING

## Slide 13
ECE 445, Fall 2021
GRAINGER ENGINEERING
Hardware Design Details: ESP32

## Slide 14
ECE 445, Fall 2021
GRAINGER ENGINEERING
Hardware Design Details: Relay Configuration

## Slide 15
ECE 445, Fall 2021
GRAINGER ENGINEERING
Hardware Design Details: OLED

## Slide 16
Modular design for testing and development
OLED (SSD1306)
  Adafruit library
  ESP32 I2C Bus
Darlington Array programmed to receive brute inputs and translate
  Relays fed by converted signal from Darlington Array
ECE 445, Fall 2021
GRAINGER ENGINEERING
Software Design Details

## Slide 17
1. The relay subsystem must be able to switch between the different solar cell configurations:
128-cells (AD)
32-cells (CD)
64-cells (BC)
ECE 445, Fall 2021
GRAINGER ENGINEERING
Requirements and Functional Tests
Breadboard | PCB
128 Cells | 128 Cells
32 Cells | 32 Cells
64 Cells | 64 Cells

## Slide 18
ECE 445, Fall 2021
GRAINGER ENGINEERING
Requirements and Functional Tests
2. The ESP32 can communicate the immediate solar panel parameters to the OLED display

## Slide 19
Monitoring
Subsystem
ECE 445, Fall 2021
GRAINGER ENGINEERING

## Slide 20
Inputs from relay configuration
  POS_output
  NEG_output
Outputs to ADC
  VOLT_output
ECE 445, Fall 2021
GRAINGER ENGINEERING
Hardware Design Details: Voltage Monitoring
Outputs to ESP32
  VOLT_Output (GPIO 15)

## Slide 21
Inputs from Voltage Divider
  VOLT_output
Outputs to ESP32
  I2C Bus (SCL, SDA)
Isolation
ECE 445, Fall 2021
GRAINGER ENGINEERING
Hardware Design Details: ADC

## Slide 22
Inputs from relay configuration
  Current_output
  POS_output
Outputs to ESP32
  Current_output_voltage (GPIO 2)
Galvanically Isolated
ECE 445, Fall 2021
GRAINGER ENGINEERING
Hardware Design Details: Current Monitoring

## Slide 23
Inputs from external thermocouples
Outputs to ESP32
  Temp_Output
ECE 445, Fall 2021
GRAINGER ENGINEERING
Hardware Design Details: Thermocouple Monitoring

## Slide 24
Modular design for testing and development
Thermocouples:
  DallasTemperatures library
  Single datapath for ESP32 measurement
Current Sensor:
  ESP32 ADC input
  Calibration: 1.0279x - 0.5137
Voltage Measurement:
  ESP32 ADC input
  Calibration: 0.9304x - 0.0337x^2 - 0.0124
ECE 445, Fall 2021
GRAINGER ENGINEERING
Software Design Details

## Slide 25
1. The ADC Converter should output a 16 bit digital code to our ESP32 that corresponds to the analog input into the IC once decoded.
MCP3428 Device Code: 1101
ECE 445, Fall 2021
GRAINGER ENGINEERING
Requirements and Functional Tests

## Slide 26
2. The voltage divider must be able to step down input voltages within the ranges of 0V - 85.6V and corresponding output voltages within the range of 0V - 3.3V
ECE 445, Fall 2021
GRAINGER ENGINEERING
Requirements and Functional Tests

## Slide 27
3. The current sensor must accurately read the current of the relay output within an error range of 1.5%
ECE 445, Fall 2021
GRAINGER ENGINEERING
Requirements and Functional Tests

## Slide 28
4. Thermocouples should measure values between the range -10°C and 85°C within an accuracy of ± 0.5°C
ECE 445, Fall 2021
GRAINGER ENGINEERING
Requirements and Functional Tests

## Slide 29
“Research Hub”
Subsystem
ECE 445, Fall 2021
GRAINGER ENGINEERING

## Slide 30
Webpage Front-end implementation: Django Framework
  User Authentication - django.contrib.auth.urls
  Observation data - ManyToOne model relationships
  Data Visualization - plotly Python Library
Server Back-end implementation: Django ORM and Django-REST Framework
ESP32 HTTP Communication:
  Observation data - WiFi.h and HTTPClient.h
  Configuration inputs - WiFi.h and ESPAsyncWebServer.h
ECE 445, Fall 2021
GRAINGER ENGINEERING
Design Details

## Slide 31
Front-end website should successfully route between pages and display solar panel data based on security and observation use cases
Working user authentication on the remote portal that restricts Research Hub access to allowed members (ECEB personnel) only
ECE 445, Fall 2021
GRAINGER ENGINEERING
Requirements and Functional Tests

## Slide 32
3. The back-end of the Django framework should have HTTP communication ability (2-way POST requests)
4. The ESP32 microcontroller should have HTTP communication ability (2-way POST requests)
ECE 445, Fall 2021
GRAINGER ENGINEERING
Requirements and Functional Tests

## Slide 33
5. Real-time observed data that is received should be processed correctly for plot/visualization updates for the specific panel
6. User-input configuration settings should be panel-specific and submission should trigger back-end communication
ECE 445, Fall 2021
GRAINGER ENGINEERING
Requirements and Functional Tests

## Slide 34
Successes and Challenges
PCB Connections:
  Pull up resistors
  OLED shorting
  ADC Bypass
  Enable Pin
  Linear Regulators
  Darlington Array
Software Interface:
  WiFi connection on independent power supply
ECE 445, Fall 2021
GRAINGER ENGINEERING
Challenges:
Successes:
All 4 subsystems working independently
Successful hardware integration (3 subsystems)

## Slide 35
Conclusions and Future Work
ECE 445, Fall 2021
GRAINGER ENGINEERING
Updating our PCB with correct internal connections
Testing further with different ADC components to achieve isolation
Establish reliable independent ESP32 WiFi connection
Visually advancing our Research Hub interface

## Slide 36
Special Thank You!
ECE 445, Fall 2021
GRAINGER ENGINEERING
Our TA, Evan Widloski
Our sponsor and guide, Professor Banerjee
  Kevin Colravy
  Bonhyun Ku
Our mentor, Professor Schuh
And, the entire ECE 445 team!

## Slide 37
Thank you!
Any Questions?
ECE 445, Fall 2021
GRAINGER ENGINEERING